INVOICE #:	19-088  			            		Date: 10/27/2019

Billing Address:							Job Location:

CMI Management                                             CSS# 21016

5285 Shawnee Rd. Suite #510                          NY024

Alexandria, VA 22312

Supply Labor and materials to repair lighting control units room 215

Tested system found one motion sensor not operating control relays seem to stick closed and keep lights on. Was able to make them operate after resetting all ceiling sensors and tapping relays worked randomly checked a few times so did Vinny Giordanno early in mornings.

Room 217 is a mechanical room. Did you mean room 219

Checked room 219 tested all ceiling sensors and found one to be defective new sensor supplied by Vinny Giordanno.

Supply labor 0ne Master licensed Electrician    8 hours X $155.00

Total:  $1,240.00

Four control relays                                                 Total:  $  312.00

One ceiling sensor                                                  Total:  $  144.00

TOTAL AMOUNT DUE:  $1,696.00