Main Office Ph: (518) 406-5439

WWW.TECHPLUSLLC.COM

6 Hearthside Drive

Technology Plus LLC

Service: Jeff Baxter

Ph: (518) 703-4590

jeff@techplusllc.com

|  |  |  | Ref # | Date | P.O. Number |
| --- | --- | --- | --- | --- | --- |
| Ballston Lake, NY 12019 | Model | Serial # | Service | 7/25/2022 | WO-17635 |
|  | INN800 | G-13-1541 | Technician | Jeff Baxter |  |
| Service Location | INN800 | G-13-1542 | Customer I Bill To |  |  |
| US Army Reserve NY060 Aerco Water heaters 1201 Hillside Ave. Schenectady, NY 12309 |  |  | CMI Management |  |  |

Equipment Information

Service Report

THIS IS NOT AN INVOICE

Description of Services

Mileage out:	Mileage in:

Saratoga, NY ***

| wi |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Service: Flame loss during ignition G-13-1541. Checked ignition controls on water heater ignition board, transformer, ignitor, a |  |  |  |  |  |
| And ssov actuator. Found faulty SSOV not opening gas valve actuator needs replacement. G-13-1542 Air/flow fault checked blower |  |  |  |  |  |
| Functions all ok. condensate stones impacted causing random air/flow faults from back pressure. PMC boards in each of the units |  |  |  |  |  |
| units are having fluctuating readings. |  |  |  |  |  |
| Recommend changing PMC boards for proper unit operation (both units). |  |  |  |  |  |
| Recommend SSOV actuator replacement. |  |  |  |  |  |
| Recommend 24 Month Preventative Maintenance be done on both units. |  |  |  |  |  |
| Item | Qty | MATERIALS |  | Each | Amount |
|  | 4 | Labor |  | $130.00 - | 520.00 - |
|  | 46 | mileage |  | $1.75 - | 80.50 - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
|  |  |  |  | $ - | - |
| Add Per Diem per: https://www.perdiem101.com/conus/2021 |  |  |  |  |  |
| Minimum Billing 4Hrs. For Emergency Callouts |  |  | Travel add actual miles under quantity |  |  |
| SERVICE RATES: $130/Hr Mon-Fri 8-5PM, $175/Hr OT after 5pm, $230Hr Weekends & Holidays MILEAGE RATES: $1.50 mile +$120/Hr. from Saratoga Springs,NY Applicable taxes not incl. Inclincluded *** |  |  |  | Sub Total $ - |  |
|  |  |  |  | Tax $ - |  |
| Customer Signature and Date |  |  |  | Total $ - |  |
| Print Customer Name, Phone #, & Email address |  |  |  |  |  |