Drinking Water Storage Tank

The contractor shall provide all plant, labor, equipment, tools, materials, supervision, and transportation to accomplish the following work, which consists of: the disinfection of 2 wells by New York State Department of Conservation certified well driller, IAW with  Environmental Conservation Law (ECL) §15-1525 , disinfection of the distribution system & disinfection of 2 storage tanks by a New York State Department of Health (DOH) certified water operator with a minimum system classification of Class C.   The storage tank disinfection shall be conducted in accordance with American Water Works Association Standard C652, Sec 4.3, Method 3. 3. The contractor shall purchase and only utilize NSF Certified sodium hypochlorite, 12.5% or greater concentration. The contractor shall demonstrate proper disinfection by utilizing a New York Department of Health Certified laboratory for two successive sets of samples taken for Total Coliform, taken at 24-hour intervals, that indicate microbiologically satisfactory water before the facility is placed into operation. The contractor shall ensure that the chlorinated water is not discharged to the storm water or sewer system until the total chlorine levels is measured at less than 1 mg/L. The contractor shall set up and adjust the peristaltic chemical feed pump for the Sodium Hypochlorite so that the parameter reading for the chlorine residual is between .2 and .4 ppm in the distribution system. The contractor shall ensure that the minimum working pressure in the distribution system should be 35 psi (240 kPa) and the normal working pressure should be approximately 60 to 80 psi (410 - 550 kPa), upon placing the wells & storage tanks back into operation. Note the 2 storage has frogs in them they need to be removed to!

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY011 |  |  |  |  |  |  |  |  |
| Disinfection of the distribution system |  |  |  |  |  |  |  |  |
| CSS #25336 - CMI # 8696 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 7.07.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 190.00 | 8 |  |  |  |  |  | $ 1,520.00 |
| 2 guys 4 hours each |  |  |  |  |  |  |  |  |
| 1.2 Bacteria Samples |  |  |  |  | $ - | $ - | $ - | $ 270.00 |
| 2 samples back to back days |  |  |  |  |  |  |  |  |
| 1.3 Certified |  |  |  |  |  |  |  | $400.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,190.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 95.00 | 1 |  |  |  |  |  | $ 95.00 |
| Grand Total |  |  |  |  |  |  |  | $ 2,285.00 |