EMERGENCY - Tiger pumps are working but are not pumping water, they are screeching CSS 31545 NY011 Bullville USARC no water going to pump house pump are making a loud noise have 150 drilling today can’t use the rest room no water or drinking water to emergency.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY011 |  |  |  |  |  |  |  |  |
| Tiger pumps are working |  |  |  |  |  |  |  |  |
| CSS #31545- CMI #14392 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.21.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 266.00 | 5.5 |  |  |  |  |  | $ 1,463.00 |
| 1.2 Misc |  |  |  |  | $ - | $ - | $ - | $ 117.04 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,580.04 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |
| Grand Total |  |  |  |  |  |  |  | $ 1,580.04 |

Note: This call has been completed. Work performed on Sunday EMERGENCY Rates.

Tech arrived on site and found that the call was for the Domestic Water Booster pump shutoff & Storage tanks at approx. 800 gallons each. Well pumps were not filling the tanks & chlorine feed pump controller plugged into a lead cord and coiled up outside of the overhead door. Tank on right had a disc on the bottom of the tank that tech believed is to trigger the sensors and should be floating around fill pump. Tech checked all GFI outlets and found that none of them will reset to operate the chlorine pump except the 1 under the catwalk that defective sump pump is plugged into.

Tech called CMI Manager and spoke with Joe Bayne, he instructed Joe that a Licensed Water plant operator needs to be called out to diagnose.