EMERGENCY Service Call.

No power in OMS Building. USARC has power on same site.

All Bright Electric responded to Emergency call.

They found 2 MV fuses blown in the MV Switch Gear for the OMS Building.

A tree limb weighed down by ice shorted two phases of the overhead MV feed to the OMS Building.

Replaced the 2 fuses and the power was restored to the building.

CMI gave verbal approval because the freezing weather and drills scheduled at the site that weekend.

** Additional**

The on-site staff was advised to have the tree removed to stop any further occurrences.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY011 |  |  |  |  |  |  |  |  |
| No power in OMS Building |  |  |  |  |  |  |  |  |
| CSS #34448 - CMI #16305 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 02.15.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 208.32 | 4 |  |  |  |  |  | $ 833.28 |
| 1.2 Fuses 2 x 685.55 |  |  |  |  | $ - | $ - | $ - | $ 1,371.10 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,204.38 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 2,204.38 |