Initial: Compressor in OMS mechanical will not hold pressure. Moisture relief valve kicking in at about 50psi and will not hold any additional pressure.

*After installing and initiating operation he found debris fouling the blowdown on the coalescing air filter assembly.

Proposal to:

1. Replace filter assembly drain valve and filter cartridge.

2. Test operation.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional funding |  |  |  |  |  |  |  |  |
| NY011 |  |  |  |  |  |  |  |  |
| Additional repairs needed |  |  |  |  |  |  |  |  |
| CSS #90202 - CMI #21043 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 01.17.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 150.00 | 5 |  |  |  |  |  | $ 750.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 473.45 |
| 1.3 Trip |  |  |  |  |  |  |  | $ 75.00 |
| 1.4 Shipping |  |  |  |  |  |  |  | $ 25.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,323.45 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |

| 2.1 CE Incurred |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Grand Total |  |  |  |  |  |  |  | $ 1,323.45 |