EMERGENCY Request

Repair Air Conditioning unit.  Unit goes off on high suction temperature. Will not continue to run.

Proposal to:

Remove both sensors and install new factory type Trane sensors.

Repair Air Conditioning unit.  Unit goes off on high suction temperature. Will not continue to run. Diagnosed 100-ton Air cooled Trane chiller, work consisted of plugging in computer lap top to diagnose system alarm and problems, took temperature readings at suction line where suction temperature sensor is located to verify sensor malfunction. Sensors were defective.

** Sensors will be ordered from Trane **

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional Funding |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Repair Air Conditioning unit. |  |  |  |  |  |  |  |  |
| CSS #1859 - CMI #18691 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 07.27.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 1,250.00 | 1 |  |  |  |  |  | $ 1,250.00 |
| 1.2 Trane temp sensors |  |  |  |  | $ - | $ - | $ - | $ 389.00 |
| 1.3 Freon |  |  |  |  | $ - | $ - | $ - | $ 250.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,889.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  | $ 500.00 |
| Grand Total |  |  |  |  |  |  |  | $ 2,389.00 |