| Additional Funding Request |  |
| --- | --- |
| NY024 | CSS #21016 WO 5601 ASSET # |
| Description of Repairs | Tested system found one motion sensor not operating control relays seem to stick closed and keep lights on. Was able to make them operate after resetting all ceiling sensors and tapping relays worked randomly checked a few times so did Vinny Giordano early in mornings. |
| Diagnosis: Initial Work Order | Trouble shoot and repair motion sensing lighting system Lights are constantly on in rooms 215 and 217. Both are large common areas ( 20 +Fixtures ) |
| Explanation of Additional Costs for Repairs | N/A |
| Additional Labor Cost to Perform Repairs | $1,240.00 (8MH @ $155.00/MH) |
| Additional Material Cost to Perform Repairs | $456.00 |
| Shipping | N/A |
| Total Cost of Repair | $1,696.00 |