Sent over Ryan Linn, safety relief valve spindle not vertical as required

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| safety relief valve spindle not vertical |  |  |  |  |  |  |  |  |
| CSS #27682 - CMI #10290 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 12.07.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor 1 Mechanic 1 helper 5 hours |  |  |  |  |  |  |  | $ 700.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 468.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,168.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ 350.00 |
| Grand Total |  |  |  |  |  |  |  | $ 1,518.00 |

Proposal to:

Removing violations from boiler inspection to pass state inspection. Completely re-pipe both safety relief valves on both hydronic type Lockinvar boiler. Both safety relief valves are mounted on a horizontal location. Must repipe safety pressure relief valves on vertical. Existing location can cause sediment to enter safety relief valve and cause relief valve not to function properly. As far as service disconnect on boiler to be able to properly isolate and shut down boiler, there is an isolation safety switch provided by manufacturer located on boiler. This will properly be marked to show location of this existing switch.

Isolate existing direct vented boiler. Draining down all glycol after isolation of system to remove safety pressure relief valve, completely re-pipe to install one relief valve in vertical location. Pump in new glycol (non toxic) to fill up boiler, remove all air out of boiler before opening up to main system.