Tech was on site working on Triad Boilers and was asked to look at the Trane Chiller.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Repair Trane chiller |  |  |  |  |  |  |  |  |
| CSS #30871 - CMI #13340 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 06.01.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 125.00 | 8 |  |  |  |  |  | $ 1,000.00 |
| 1.2 Commercial coil cleaner |  |  |  |  | $ - | $ - | $ - | $ 35.25 |
| 2 gallons |  |  |  |  |  |  |  |  |
| 1.3 Misc |  |  |  |  | $ - | $ - | $ - | $ 200.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,235.25 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |
| Grand Total |  |  |  |  |  |  |  | $ 1,235.25 |

Proposal to:

servicing of chillers in Fort Wadsworth. 1 100 ton air cooler chiller in building 356. 1 Trane air cooler chiller in building 356

Trane chiller, remove all access panels on outside condenser to gain access to condenser coil. This will consist of unbolting each access panel individually to get to condenser coil, use special Trane acid type coil cleaner to properly clean condenser coil to provide proper heat transfer. Comb fins. Cannot check refrigerant levels until outside temperature reaches 85 degrees ambient. Reinstall all access panels with securing bolts to put back into operation.