Repair AC Chillers Building 356 Replace Suction Temperature Sensor Add 410 Refrigerant Building 208 Replace Suction Temperature Sensor.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Repair AC Chillers Building 356 |  |  |  |  |  |  |  |  |
| CSS #31527 - CMI #14874 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.21.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 175.00 | 6 |  |  |  |  |  | $ 1,050.00 |
| 1 computer tech x 3 hours |  |  |  |  |  |  |  |  |
| 1 Labor tech x 3 hours |  |  |  |  |  |  |  |  |
| 1.2 Suction temperature sensors |  |  |  |  | $ - | $ - | $ - | $ 579.80 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,629.80 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |
| Grand Total |  |  |  |  |  |  |  | $ 1,629.80 |

Note: This wo has been completed. Tech was on site for another issue and was asked to look at this. It was approved while he was on site by Carlo Accardi and a CSS # issued after completion.

Diagnosed both 100-ton Air cooled Trane chillers, work consisted of plugging in computer laptop to diagnose system alarm and problems, took temperature readings at suction line where suction temperature sensor is located to verify sensor malfunction. Both sensors were defective Removed both sensors and installed new factory type Trane sensors.

- Work consisted of replacing both suction temp sensors for both chillers to keep all stages running to provide proper temp to both chillers