Repair / Service BMS system Bldg 356/ 358. Unable to test heating system prior to seasonal change over.

EMCOR found - No issues with boilers or bms controlling them. Vinny needed help operating bms. Showed him how to navigate Niagara based controls in 356. Building needs new supply water temp sensor. Went to another building with delta controls. No front end. Will need to get delta onsite to look

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Service BMS system Bldg 356/ 358 |  |  |  |  |  |  |  |  |
| CSS #32667 - CMI #15207 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 03.11.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 75.00 | 16 |  |  |  |  |  | $ 1,200.00 |
| 1.2 Trane sensors - x2 |  |  |  |  | $ - | $ - | $ - | $ 372.72 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,572.72 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 1,572.72 |

Proposal to:

Replace both chilled water sensors on main chilled water lines, feeding Trane outdoor air-cooled chiller, work consists of isolating both supply and return chilled water lines, draining glycol and removing old sensors and reinstalling new sensors reconnecting wiring re-filling with glycol removing all air out of lines to put system back into operation.

** Note - If any reprogramming is needed to Trane chiller there will be an additional charge of $2,000, this will cover the cost for a technician for 1 day with truck expense