Repair Triad High Efficiency Boiler. On Sunday there was a power outage on Staten Island. Boiler LCD is showing 02 code.

Proposal to:

After troubleshooting Triad condensing type boiler located in basement mechanical room bldg #208 found hi limit safety control not operating at proper shut-off temperature must replace control also clean combustion screen and set parameters on Honeywell control module.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Repair Triad High Efficiency Boiler. |  |  |  |  |  |  |  |  |
| CSS #34774 - CMI #16640 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 03.15.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 75.00 | 20 |  |  |  |  |  | $ 1,500.00 |
| 1 Mechanic - 1 helper 10 hrs each |  |  |  |  |  |  |  |  |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 368.92 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,868.92 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |
| Grand Total |  |  |  |  |  |  |  | $ 1,868.92 |