Building 208 First floor west side 15 Ton AC unit will not run.

This unit supports the 3 Classrooms on the first floor.  Multiple units are on BA this weekend and are using those classrooms.

Emergency service call,

Responded  Thurs 7/20 had to turn around the rain was unbearable. Received call from Vinny came Friday, Installed gauge set found system short of refrigerant, Added 26.5 lbs of R-410A brought system to proper operating temperatures and pressures. Checked classroom temperatures ok came down 5 degrees

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional funding |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Building 208 First floor west side |  |  |  |  |  |  |  |  |
| CSS #94362 - CMI #23754 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 07.24.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor |  |  |  |  |  |  |  | $ 400.00 |
| 1.2 R22 26.5 lbs |  |  |  |  | $ - | $ - | $ - | $ 1,987.50 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,387.50 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 2,387.50 |