** EMERGENCY**

Chiller is inoperative ( High Suction Temperature ) Building has no Air Conditioning.

Proposal/Invoice to:

Found outside chiller completely down-#1—outside condenser loaded with grass clippings the landscapers are not using a collecting bag on their machine blowing the grass into the outside condenser coil causing it to clog coil and possibly causing these hi temperature safety to malfunction. Vinny and I were able to get circuit #2 operating. I replaced suction temperature safety sensors and added 7.5 lbs. of R-410A refrigerant.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional funding |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Chiller is inoperative |  |  |  |  |  |  |  |  |
| CSS #95027 - CMI #24290 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.11.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 12 |  |  |  |  |  | $ 1,200.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,000.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,200.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 2,200.00 |