SEWAGE BACKUP IN THE BOILER ROOM.  SUMP PUMP HAS FAILED. CMI onsite for a different repair.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY054 |  |  |  |  |  |  |  |  |
| SEWAGE BACKUP IN THE BOILER ROOM |  |  |  |  |  |  |  |  |
| CSS #32522 - CMI #14875 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.13.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 80.00 | 3 |  |  |  |  |  | $ 240.00 |
| 1.2 Sewage Pump |  |  |  | $ 359.96 | $ 25.20 | $ 385.16 | $ 77.03 | $ 462.19 |
| 1.3 Shipping |  |  |  |  |  |  |  | $ 45.00 |
| 1.4 Misc |  |  |  |  |  |  |  | $ 120.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 867.19 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 80.00 | 2 |  |  |  |  |  | $ 160.00 |
| Grand Total |  |  |  |  |  |  |  | $ 1,027.19 |

CMI tech Mike was on site performing the Boiler PM when he was asked to look at this unit by the AFOS Ron. Mike found that the float has connection issues, he was able to make a temporary repair to the float. But upon further inspection he found that the entire pump is rotted and is covered in grease. Pump is over 10 years old.

Note: The pump is currently working but if there is a heavy rain it could cause issues with flooding.