Backup Generator will not start. Need to have it serviced by the electrician that installed it.

| Provide complete service/ repairs of Kohler Gas Generator |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Repair all control wiring that was damaged and rewire |  |  |  |  |  |
| Remove engine oil & replace with synthetic oil |  |  |  |  |  |
| Remove engine coolant, flush, replace coolant |  |  |  |  |  |
| Remove & replace Spark plugs |  |  |  |  |  |
| Remove & replace air cleaner element |  |  |  |  |  |
| Remove & replace worn V-belt |  |  |  |  |  |
| Check out all electrical terminations on unit. |  |  |  |  |  |
| Install new charger to maintain battery |  |  |  |  |  |
| Install New Battery |  |  |  |  |  |
| Inspect Automatic Transfer Switch for proper operation |  |  |  |  |  |
| Run generator for proper operation |  |  |  |  |  |
| Test Automatic transfer switch under load for proper operation |  |  |  |  |  |

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional Funding Request |  |  |  |  |  |  |  |  |
| NY059 |  |  |  |  |  |  |  |  |
| Backup Generator will not start. |  |  |  |  |  |  |  |  |
| CSS #22139 - CMI # 6875 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 11.06.19 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 12 |  |  |  |  |  | $ 1,200.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,299.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,499.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $2,499.00 |