Repair Ductless Split AC Unit in receiving office.
This unit is wired off a light switch with a motion sensor. Every time the light turns off the AC unit and condensate pump shut off which makes a puddle on the floor.

Proposal to:

Found condensate pump power tied into lighting occupancy sensor.

When the light goes out, the pump would not work.

Rewire pump to fully powered outlet.

Put units back into service.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional funding |  |  |  |  |  |  |  |  |
| NY059 |  |  |  |  |  |  |  |  |
| Repair Ductless Split AC |  |  |  |  |  |  |  |  |
| CSS #94232 - CMI #24276 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 08.15.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 120.00 | 4 |  |  |  |  |  | $ 480.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 195.92 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 675.92 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred processed |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 675.92 |