Two heat pump units, HP2-28 and 2-33 are not communicating with the building controls. Neither thermostat has a reading. If we have an electrical issue with both units.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Two heat pump units, HP2-28 and 2-33 |  |  |  |  |  |  |  |  |
| CSS #18784 - CMI # 6052 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 12.05.19 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 108.00 | 6 |  |  |  |  |  | $ 648.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 47.05 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 695.05 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 108.00 | 4 |  |  |  |  |  | $ 432.00 |
| Grand Total |  |  |  |  |  |  |  | $ 1,127.05 |

Proposal to supply all labor and material needed to complete the following

• Inspect Heat Pumps

• HP 2-28: Water supply valve stuck. Unthread and oil.

• HP 2-26: Low on Nitrogen, charge. Locate leak – will provide separate proposal

• HP 2-33: Bad fan relay – replace

- Test Operation