Repair cooling tower, multiple leaks were found during the annual start up performed by BPI. 3 leaks; One on the 1' copper fill line elbow, one on the fill line 3/4' solenoid valve and one on the 2' drain line beneath the unit.

Repair cooling tower fill valve and water line

Isolate and drain water line

Remove pipe covering as necessary

Remove failed fill valve and cracked piping

Furnish and install new valve and associated piping

Pressure test

Replace pipe covering that was removed

Put units back into service

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional funding |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Repair cooling tower |  |  |  |  |  |  |  |  |
| CSS #700 - CMI #18262 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 07.07.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 115.00 | 8 |  |  |  |  |  | $ 920.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 481.68 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,401.68 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 1,401.68 |