NO Heat, 2nd floor of USARC

No heat on the majority of second floor of USARC. Multiple Heat pump units (4) will not go into heating mode. Boilers are operational and discharging at set point temps.  I have tried to switch HP's on BMS to heat mode with no success.

Proposal to:

Service to heat pumps HP 2-19 and bldg. system

Found faulty actuator on control valve

Remove failed actuator

Install new actuator

Cycle units to check operations

Put system into operation

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional Funding |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| NO Heat, 2nd floor of USARC |  |  |  |  |  |  |  |  |
| CSS #92291 - CMI #21459 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 03.08.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 120.00 | 8 |  |  |  |  |  | $ 960.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 282.97 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,242.97 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  | $ 600.00 |
| Grand Total |  |  |  |  |  |  |  | $ 1,842.97 |