The training facility kitchen freezer for the 411th EN BDE is not working and all the food inside has now spoiled.

Tech was on site 11/04 to replace the compressor.

After the installation of the compressor the unit was not staying to temp. He performed a diagnostic and found the evaporator coil leaking. This proposal is to perform that work.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY116 |  |  |  |  |  |  |  |  |
| Training facility kitchen freezer |  |  |  |  |  |  |  |  |
| CSS #26972 - CMI #10700 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 11.05.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 119.00 | 5.5 |  |  |  |  |  | $ 654.50 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 623.09 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,277.59 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 1,277.59 |