After replacing condenser unit was running hot. EMCOR diagnosed the issue and found filter dryers inside on the head. They need to be changed.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| Replace filter Dryers for Unit 1 |  |  |  |  |  |  |  |  |
| CSS #20470 - CMI #10238 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 8.24.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 158.11 | 9 |  |  |  |  |  | $ 1,423.00 |
| 1.2 Materials |  |  |  |  | $ - | $ - | $ - | $ 277.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,700.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 1,700.00 |

Proposal to:

The scope of work for the change order will include materials and labor for the following:

 Pump down refrigerant and isolate Liebert air handler

 Remove and replace both Liebert air handler filter driers

 Re-pressurize system

 Test and place system back into normal operation