Repair domestic hot water heater in OMS.

We propose to furnish the necessary labor, material, and supervision required to replace gas valve and properly set up gas conversion LP to natural. It is to my understanding the facility was originally LP and converted to natural. Original conversion was not properly done.

Our proposal is based on the following:

1. Remove existing defective LP gas valve.

2. Install correct natural gas valve.

3. Verify orifices are correct for natural gas.

4. Perform start up procedure per manufacturer.

5. Test and adjust gas and manifold pressures.

6. Perform combustion analysis to manufacturer specifications.

7. Install new manufacturer supplied boiler plate with conversion info.

Our proposal excludes the following:

- Parts or materials not herein listed.

- 2. Labor to replace parts or materials not here in listed.

- 3. Permits or fees.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| Repair domestic hot water |  |  |  |  |  |  |  |  |
| CSS #297 - CMI #17201 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 05.13.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 150.00 | 8 |  |  |  |  |  | $ 1,200.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 445.00 |
| 1.3 Misc |  |  |  |  |  |  |  | $ 50.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,695.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 1,695.00 |