Flagpole spotlight does not function. Flag is not illuminated at night.:

Proposal for additional diagnostic:

| 1. Lighting for exterior walkway, flagpole, exterior building lighting does not work. |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Additional troubleshooting of circuit will need to be performed. Wiring underground to |  |  |  |  |  |  |  |
| Quazite junction box located in lawn area will have to be traced to Bollard lighting fixtures, |  |  |  |  |  |  |  |
| flagpole lighting, wall pack lighting to determine where the problem exists. Each fixture |  |  |  |  |  |  |  |
| will have to be removed from pedestal to inspect terminations. As built drawings do not |  |  |  |  |  |  |  |
| detail how the wiring is run from fixture to fixture, or where the feed originates. |  |  |  |  |  |  |  |
| 2. Photocells need to be replaced; they do not stay in swivel position due to screws being |  |  |  |  |  |  |  |
| stripped out of holder. |  |  |  |  |  |  |  |

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional Funding |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| Flagpole spotlight does not function |  |  |  |  |  |  |  |  |
| CSS #89946 - CMI #19365 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.27.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 110.00 | 8 |  |  |  |  |  | $ 880.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 61.86 |
| 1.3 Markup |  |  |  |  | $ - | $ - | $ - | $ 12.37 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 954.23 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  | $ 450.00 |

| Grand Total |  |  |  |  |  |  |  | $ 1,404.23 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |