diagnose and repair Glycol leak.  The leak is in between the roof top mechanical room and the assembly hall ceiling.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| diagnose and repair Glycol leak |  |  |  |  |  |  |  |  |
| CSS #30961 - CMI #13344 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 6.10.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 1 |  |  |  |  |  | $ 100.00 |
| 1.2 R-410 Refrigerant |  |  |  |  | $ - | $ - | $ - | $ 1,250.00 |
| 25 pounds at $50 a pound |  |  |  |  |  |  |  |  |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,350.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  | 1 |  |  |  |  |  | $ - |
| Grand Total |  |  |  |  |  |  |  | $ 1,350.00 |

This work has been performed:

Both circuits needed in order to cool.

check refrigerant levels on Trane Outdoor chiller located behind building, added 1 tank of R410-A to circuit number 1, 12 pounds to circuit #2, 13 pounds to circuit #1 checked temperatures and pressures, system running well.