From: Joe Bayne <joe.bayne@cmimgmt.com> 
Sent: Tuesday, April 21, 2020 10:59 AM
To: John Sullivan <jasullivanelect@gmail.com>
Cc: Vanessa Fernandez <vanessa.fernandez@cmimgmt.com>
Subject: O&A NY011, CSS 21967, Wo 7919

Good morning john,

Please provide an ETA on the parts when available. The contracting officer has approved the following additional work as requested by the 99th as priority work, and shall be completed during the  COVID-19 Emergency in order to ensure the back-up generator functions properly when needed, and operational for the current building commissioning requirement for this facility:

Site NY011

CSS # 21967

CMI WO # 7919

Asset # NA

Scope:  Provide the following repairs to existing generator to make it fully operational: relocate hard-to-reach battery racks from under back of generator; repair cracked exhaust flex; re-configure engine angle needs and straightened out to keep new flex from breaking; install new 24 vdc 15-amp battery charger; rebuild/replace engine starter or replace bad battery; certify repair work to ensure the generator functions properly.

Joe Bayne

Project Manager / 99th - Region 2

5285 Shawnee Road Suite #510

Alexandria, VA  22312

703-738-5304

joe.bayne@cmimgmt.com

This message (including any attachments) contains confidential or privileged information intended for a specific individual and purpose, and is protected by law.  If you are not the intended recipient, please notify the sender at (703) 738-5300.  Any disclosure, copying, or distribution of this message, or the taking of any action based on it, is strictly prohibited.