Fahrenheit Inc.

85 Farless Avenue

Old Bridge, New Jersey 08857

Telephone (732) 673- 9318  E-mail: Celcius60@aol.com

	PROPOSAL
	X

	INVOICE
	

	DIAGNOSTIC
	


Today's Date: 7/26/2022

Customer Name: Joe Bayne



	CSS/INVOICE#
18691 WO#18691 


	DATE(S) OF SERVICE


	LOCATION

Bldg 208


	JOB DESCRIPTION
Repair Air Conditioning unit.  Unit goes off on high suction temperature. Will not continue to run. Diagnosed 100 ton Air cooled Trane chiller, work consisted of plugging in computer lap top to diagnose system alarm and problems, took temperature readings at suction line where suction temperature sensor is located to verify sensor malfunction. Sensors were defective Removed both sensors and installed new factory type Trane sensors.


	PARTS
1- Trane factory suction temperature sensors  part # Cen4239

5 pounds of freon @ 50 pounds 
	COST
$389.00

$250.00

	LABOR
4 hours to clean condenser (completed)

Computer Technician - 


	COST
$500.00

$1,250.00


	TAX
	

	TOTAL
	$2,389.00


Thank you for your business


