| PROPOSAL | X |
| --- | --- |
| INVOICE |  |
| DIAGNOSTIC |  |

Today's Date: 5/27/2020

Customer Name: Joe Bayne

| CSS/INVOICE# 25141 | DATE(S) OF SERVICE | LOCATION Fort Wadsworth bldg 208 |
| --- | --- | --- |

| JOB DESCRIPTION remove damaged taco high velocity circulator pump #2. removing pump consists of removing and cutting of existing rusted bolts with cetalyn and oxygen. Disconnect the piping and coupler from the motor, There is no isolation valve on the discharge off the pump which means the drainage of the system will be difficult. existing system has 2 circulator pumps, one is defective and leaking. System needs to be drained down to change main circulator pump, time will be spent purging hot water coils and to remove air from system. Time will also consist of removing air from the system after installation which will include going to each air handler and all mechanical rooms throughout bldg 208. Each air handler will have to be bled individually to ensure no air is in the system. Installation includes lining up existing pump to pump motor. The pump motor shaft has to line up to motor shaft. |  |
| --- | --- |
| PARTS 1 Taco circulator pump model# FI1207E2CAH1LOB companion flanges and bolts 1 – 3/16 inch lovejoy coupler | COST $5617.50 $250.00 $5867.50 |
| LABOR 1 mechanic and 1 helper @ 14 hours | COST $2,500.00 |
| Diagnostic Fee | $350.00 |
| TOTAL | $8,717.50 |