Fahrenheit Incorporated

85 Farless Ave

Old Bridge N.J

Telephone (732) 673- 9318

E-mail: Celcius60@aol.com

| To: |  |
| --- | --- |
| CMI Joe Bain---356 Fort wadsworth SINY WO 15207 CSS#32667 |  |

| Date |  | Bldg 356 SINY |  |
| --- | --- | --- | --- |
| 03/09/22 |  |  |  |
| Job Description | Rate Amount |  |  |
| Replace both chilled water sensors on main chilled water lines, feeding Trane outdoor air cooled chiller, work consists of isolating both supply and return chilled water lines,draining glycol and removing old sensors and reinstalling new sensors reconnecting wiring re-filling with glycol removing all air out of lines to put system back into operation. | Materials required: 2-Trane sensors 10,000ohm resistance Model # SEN02133-------$186.36 each—total--$372.72------1 day 1-mechanic---1--helper $1,200. If any reprogramming is needed to Trane chiller there will be an additional charge of $2,000, this will cover the cost for a technician for 1 day with truck expense. |  |  |
|  | Total proposal price—without computer tech $1,572.72 |  |  |

Thank you for your business.