Fahrenheit Inc.

85 Farless Avenue

Old Bridge, New Jersey 08857

Telephone (732) 673- 9318  E-mail: Celcius60@aol.com

	PROPOSAL
	X

	INVOICE
	

	DIAGNOSTIC
	


Today's Date: 11/23/2021

Customer Name: Joe Bayne



	CSS/INVOICE#
CSS 33548 
	DATE(S) OF SERVICE


	LOCATION

Bldg 356 & 208


	JOB DESCRIPTION
found both Triumph condensing type boiler not firing, along with Triad boiler going off on safety. Must replace low water cut off control board along with low water insertion type probes. Triad boiler, needs electrode and sensor replaced. This will stop nuisance safety failures. Condensing Triump boiler. Isolate and drain down boilers to replace low water cut off and sensing probe. Disconnect existing electronic control board and replace with new type revised control board. Must be rewired to accept new control board design. Triad boilers – must replace electrode and sensor probes. Disconnect from underneath power flame burner access panel. Pull electrode assembly out and replace with new. 

	PARTS
Triumph condensing boilers (2) – 2 low water control circuit boards # 26C3A024, 

2 low water sensing probes part TSL050C

Materials for Triad stand up chimney vented boilers – 1 is in bldg 356 and 1 is located in bldg 208 – parts needed – 1 complete electrode and flame sensor combination. Part # F30031
	COST
$550.66 x 2 – 1,101.32

$241.20 x 2 – 482.40

$959.85 x 2 -  1919.64

	LABOR
1 day for both boilers

1 day for both Triad boilers


	COST
$800.00

$800.00


	TAX
	

	TOTAL
	$.5103.36


Thank you for your business


