Fahrenheit Incorporated

85 Farless ave

Old Bridge N.J 08857

Telephone (732) 673- 9318

E-mail: Celcius60@aol.com

| To: |  |
| --- | --- |
| CMI Joe bain—Bldg 356 |  |

| Date |  | Bldg 356 rotted line feeding coil |  |
| --- | --- | --- | --- |
| 03/09/22 |  |  |  |
| Job Description | Rate Amount |  |  |
| Found rotted piping feeding heating coil located in upstairs Mezzanine, this piping is leaking and losing glycol, this line is leaking and losing glycol this line should be repaired before line ruptures. Scope of work: Isolate and drain down all glycol out of coil, remove all piping which is damaged and re-pipe with new galvanized piping and fill system up with glycol remove all air out of system. | Materials and labor required: 1-set of 1-1/4” galvanized nipples---2-1-1/4” gal close and shoulder nipples-1-1-1/4”x ¾” x 1-1/4” gal tee—2--3/4”x 3” gal nipples—1-3/4” ips ball valve—1-3/4” gal cap---1-1-1/4”gal Y strainer—1-1” gal union—1-1”x 1-1/4”gal red coupling 1-1” gal set of nipplers 1- roll of lampwick 1- container of leak lock sealant—1-1” copper x fem adapter, actylene flux and solder 95/5 ---10 gallons of non -toxic antifreeze----Total materials---$975.76 Labor 1-mechanic and helper 8hrs plus 2hrs to expedite all materials with truck expense----Total labor--$1,500 |  |  |
|  | Total propsal price--$2,475.76 |  |  |

Thank you for your business.