Fahrenheit Inc.

85 Farless Avenue

Old Bridge, New Jersey 08857

Telephone (732) 673- 9318  E-mail: Celcius60@aol.com

	PROPOSAL
	

	INVOICE
	X

	DIAGNOSTIC
	


Today's Date: 4/7/2022
Customer Name: Joe Bayne



	CSS/INVOICE#
CSS35433
	DATE(S) OF SERVICE


	LOCATION

Bldg 208 / 356


	JOB DESCRIPTION
emergency service call and repair heating system was completely down on building 208. also emergency repairs for bldg 356, pressure relief valve blowing off.
Bldg 208 found water pouring out of baseboard radiator located on first floor. Had to drain heating system located in mechanical room in sub basement. Cut out damaged piping located in radiator and replaced with new shark bite couplings. Build system install radiator covers and filled system at boiler location. 
Bldg 356 found pressure relief valve weak and blowing water out of boiler. Found damaged and defective pressure reducing valve which was allowing to much water to fill system. Installed new pressure relief valve and re-pipe to existing drain, install new B&G 25 poumd capacity pressure reducing valve. Had to re-pipe in order to accept new valve.



	PARTS

Bldg 208 Parts – 1 10ft length ¾ L tubing, 2 ¾ shark bite couplings,
Bldg 356 Parts – 1 ¾ 50 psi relief valve, 1 ¾ B&G pressure reducing valve, soder, flux, cetalyne and misc to install
	COST
$675.00

$320.00



	LABOR
bldg 208 1 mechanic 8 hours for emergency call

bldg 356 5 hours 1 mechanic and helper


	COST
$800.00 (200.00 truck expense)

TOTAL $1,000.00

$625.00


	TAX
	

	TOTAL
	$2,620.00


Thank you for your business


