## Air Compressor
PREVENTATIVE MAINTENANCE PROGRAM CHECKLIST
AIR COMPRESSOR
SITE AND BLDG #: |  |  | MECHANIC SIGNATURE: DATE:
LOCATION/RM #: WO# ASSET # |  |  | START TIME: FINISH TIME:
MANUFACTURER: MODEL #: SERIAL #:
CHECK POINT | CHECKPOINT DESCRIPTION | TASK COMPLETE |  | NOTES/ ACTIONS (IF TASK COMPLETE IS CHECKED NO, PROVIDE EXPLANATION)
|  | YES | NO
SPECIAL INSTRUCTIONS
1 | Follow lock out/tag out procedures at all times. De-energize or discharge all hydraulic, electrical, mechanical, or thermal energy prior to beginning work.
TO BE PERFORMED AT EACH INSPECTION SERVICE
1 | . Perform a visual inspection of the air system, noting any obvious leaks or portions of the air distribution network that may be subject to physical damage.
2 | Change compressor crankcase oil (annually).
3 | Clean or replace air intake filter, as needed.
4 | Check air dryer, automatic condensate drains, and air tank for proper operation. Manually blow down condensate tank if needed. Clean condenser coils and cover grills, if applicable.
5 | Inspect oil separators for any sign of oil entering the system.
6 | Inspect belt alignment and condition. Adjust or replace belts as required. Belts should be replaced in complete sets.
7 | Check motor starter contactor - inspect contacts for pitting or arcing
8 | Clean heat exchange surfaces.
9 | Check gauges to be in good condition
10 | On two stage compressor, check intermediate pressure.
11 | Test relief valves, replace if leaking . Do not readjust safety relief valves in the field.
12 | Check cut in and cut out of compressor pressure controller, readjust if necessary for proper air pressure requirements. Do not exceed ASME maximum tank pressure.
13 | Check to make sure belt guard is installed prior to putting air compressor back in service.
14 | Check if air compressor is running excessively or frequently cycling on and off (possible leaks).
Checklist compiled in accordance with:
- General Services Administration (GSA) Public Building Service. 2012. Public Buildings Maintenance Standards Final.October 1.
- Original equipment manufacturers (OEM) documentation for exact or similar assets, which can be located at (Provide Link to OEM Manual/Asset Library)
Recommended Tools, Materials, and Equipment:
1. Standard Tools - Basic
2. Belts
3. Lubricants. Consult the Material Safety Data Sheets (MSDS) for hazardous ingredients and proper personal protective equipment (PPE).
4. Fin comb
5. Vacuum cleaner commercial type
6. Test gauge
7. Ultrasonic scanner with trisonic and contact scanning modes.
Note: The technician shall perform any repairs identified during PM up to $250 (direct labor and direct material cost) per PM occurrence. For any deficiencies found
exceeding $250 open a corrective maintenance (CM) ticket and include the Asset #, WO #, photos, and a detailed discription of the deficiency.
To be perfomed by: General Maintenance Worker
Additional Notes: