## Sheet1
Proposal for Electrical Work Site Lighting Repairs
CMI Management |  |  |  |  | CSS33359
5285 Shawnee Road
Alexandria, VA. 22312
Attn: Joe Bayne
For: |  | Bullville USARC |  |  | NY011 | 2022-02-14
Location: |  | 2500 Route 17K Bullville, N.Y 10915
Scope of work involved at Bullville USARC CSS33359
1. Evaluate a Qty of ( 15 ) 30 Foot Pole mounted Security lights on main driveway for repairs
2. Existing fixtures are Metal Halide HID style. Over 50 % of the existing lights are faulty.
Transformer ballast kits and replacement bulbs would need to be replaced
3. Existing lighting is 21 years in vintage. Repairs to fixtures does not meet feasibility
due to the cost for replacement parts, and labor to rebuild, and ongoing maintenance of fixtures
Recommended actions would to replace the fixtures with New economical style
energy efficient LED fixtures producing the equivalent lumen levels
4. Automatic control of lighting needs to be repaired. Lights are currently operating
intermittently during the daytime hours. Photo control for automatic operation is faulty.
Lighting contactor has burned contacts and needs to be replaced
PROPOSAL FOR REPLACEMENT/ REPAIRS
1. Remove faulty lighting fixtures from existing locations.
2. Install a Qty of ( 15 ) New 150 Watt LED pole mounted lighting fixtures. Provide retrofit
hardware to adapt new lights to existing poles.
3. Replace photo control & lighting contactor for automatic operation
******Service Call 2/10/2022 to evaluate lighting for repairs | [5 empty] | 450
1. Qty of ( 15 ) A17 3T LED lighting fixtures @ $ 393.00 each | [5 empty] | 5895
2. Qty of ( 15 ) A17 Universal Mounting Pole Kits @ 41.65 each | [5 empty] | 624.75
3. Qty of ( 1 ) Intermatic Heavy Duty 277 Volt Photo Control | [5 empty] | 34
4. Qty of ( 1 ) Square D 3 Pole 30 Amp 277 volt Contactor/Enclosure | [5 empty] | 212
|  |  |  | TOTAL MATERIALS |  | 6765.75
Labor man hours 60 hours @ 115.00 per electrician | [5 empty] | 6900
|  |  | Service Call |  | 450
|  |  | Labor |  | 6900
|  |  | Materials |  | 6765.75
|  |  | Mark-up 20% |  | 1353.15
|  |  | Equipment Rental |  | 1941
|  |  | All Terrain 45 FT |  | 17409.9 | TOTAL PROPOSAL
Aerial Boom Lift
John A. Sullivan
Electrical Contractor Inc.
1 Pepe Road
Boonton, New Jersey 07005
973-334-0291 Fax 973-299-9398 N. J. Electrical License 7785A
Email jasullivanelect@gmail.com