| PROPOSAL | X |
| --- | --- |
| INVOICE |  |
| DIAGNOSTIC |  |

Today's Date: 8/18/2020

Customer Name: Joe Bayne

| CSS/INVOICE# TBD | DATE(S) OF SERVICE | LOCATION Fort Wadsworth bldg 208 |
| --- | --- | --- |

| JOB DESCRIPTION Diagnostic – received emergency service call. Checked out Trane outdoor liquid chiller – 100 ton. Found 2 compressors going off on high suction pressure. Adjusted refrigerant charge on circuit #1. head pressure was at 400 pounds at 75 degree outdoor temperature. Adjusted refrigerant charge to 325 which is normal for 75 degree outdoor temperatures. Circuit #2 machine goes off on alarm for high suction temperature. Spoke to factory recommend changing liquid line filter dryers and suction pressure sensor. After those 2 things are changed we can go from there. Spoke to Trane and they recommended maintenance and to change liquid line filter dryers. |  |
| --- | --- |
| PARTS 2 Liquid Line filter dryers - LLD-DHY01320 2 suction line pressure transducer (recommend replacement per maintenance) TDR00735 | COST $372.00 each – $744.00 $350.00 each – $700.00 |
| LABOR expediting materials, travel and 1 mechanic and 1 helper @ 150.00 x 12 hours | COST $1,800.00 |
| Diagnostic Fee | $350.00 |
| TOTAL | $3,594.00 |