Asset 6594, Boiler, Relief valve discharge line piping to a tee connection should be changed so it is not routed and connected to air separator. R.V. discharge line need to be independent. Change relief valve line piping. Remove tee connection so discharge line piping is independent.

Proposal to provide and perform the following:

• Cutting and separating of 2 drain lines

• 1” Copper pipe, couplings, elbows

• Start up

• Warranty

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| PA013 |  |  |  |  |  |  |  |  |
| Relief valve discharge line piping |  |  |  |  |  |  |  |  |
| CSS #15864 - CMI # 5953 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 02.19.19 |  |  |  |  |  |  |  |  |
| Asset 6954 |  |  |  |  |  |  |  |  |
| P3 Routine |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 98.00 | 8 |  |  |  |  |  | $ 784.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 92.31 |
| 1.3 Shipping |  |  |  |  |  |  |  | $ 24.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 900.31 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 98.00 | 2 |  |  |  |  |  | $ 196.00 |
| Grand Total |  |  |  |  |  |  |  | $ 1,096.31 |