| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| PA050 Indiana |  |  |  |  |  |  |  |  |
| Misc heating system repairs. |  |  |  |  |  |  |  |  |
| CSS #16538 - CMI # 7190 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 1.24.19 |  |  |  |  |  |  |  |  |
| Assets 4019, 4014 & 4405 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| Asset #4019, Entrance Vestibule |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 98.00 | 2 |  |  |  |  |  | $ 196.00 |
| 1.2 Fan Coil Motor |  |  |  |  | $ - | $ - | $ - | $ 407.93 |
| 1.3 Shipping |  |  |  |  |  |  |  | $ 24.00 |
| 2. Repair Cost |  |  |  |  |  |  |  |  |
| Asset #4014, Mr. Davis Office water flow |  |  |  |  |  |  |  |  |
| 2.1 Labor | $ 98.00 | 4 |  |  |  |  |  | $ 392.00 |
| 2.2 Schneider 2 position valve |  |  |  |  | $ - | $ - | $ - | $ 125.23 |
| 2.3 Copper Elbow, copper tees, adaptors |  |  |  |  |  |  |  | $ 75.00 |
| 2.4 Shipping |  |  |  |  |  |  |  | $ 24.00 |
| 3. Repair Cost |  |  |  |  |  |  |  |  |
| Asset # 4405 Data Room - Boiler Room Heater A |  |  |  |  |  |  |  |  |
| 3.1 Labor | $ 98.00 | 2 |  |  |  |  |  | $ 196.00 |
| 3.2 Fan Coil Motor |  |  |  |  | $ - | $ - | $ - | $ 99.59 |
| 3.3 Shipping |  |  |  |  |  |  |  | $ 24.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,955.75 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 98.00 | 4 |  |  |  |  |  | $ 392.00 |
| Grand Total |  |  |  |  |  |  |  | $ 2,347.75 |

Misc heating system repairs. Check uni-vent operation in: Entrance vestibule -fan motor intermittent operation, Mr. Davis office -water flow valve does not operate and appears corroded shut., Data room – no heat from unit, Mechanical room prop heater -  though there appears to be two new motor operated valves installed by CMI, there still is no hot water flow to the prop heater coil, fan just blows cold air. AHU in old range does not operate - I think the fan motor or its controls are bad. Unit froze up earlier this summer which would indicate fan not operating.  CM #6647 WO# 7105 Asset 4014 - this is listed in CSS 16538 CM #6647 WO# 7106 Asset 4019 - this is listed in CSS 16538 CM #6647 WO# 7107Asset 4405 - this is listed in CSS 16538 - Work was done on this unit in August (electrically operated valves replaced) and is not working

This proposal is for Assets 4019, 4014 & 4405

Entrance Vestibule Asset # 4019:

- Provide & replace motor in vestibule entrance way for the Fan Coil Unit.

- Start up

- Warranty

Mr. Davis Office Water Flow Valves Asset # 4014:

- Drain Unit

- Repair hose to unit so water has somewhere to drain

- Remove defective valve & body

- Pipe & fittings

- Start up

- Warranty

Data Room – Boiler Room Unit Heater A Asset # 4405:

- Provide & replace motor in vestibule entrance way for Fan Coil Unit

- Start up

- Warranty