Boiler #2 and #3 - The safety relief valves are not installed with the spindle in the vertical position. The safety relief valves shall be re-piped so the spindles are installed in the vertical position.

Proposal is labor and materials to re-pipe boilers #3 and #4 safety valves. If the isolation valves do not hold the boiler loop will need to be drained. If loop needs to be drained we will send a revised quote.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| WV020 |  |  |  |  |  |  |  |  |
| Boiler 2 & 3 - The safety relief valves |  |  |  |  |  |  |  |  |
| CSS #15990 - CMI # 6422 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 1.22.19 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 115.00 | 8 |  |  |  |  |  | $ 920.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 185.12 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 1,105.12 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |
| 2.2 Truck Charge |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 1,105.12 |