| PROPOSAL |  |
| --- | --- |
| INVOICE | X |
| DIAGNOSTIC |  |

Today's Date: 4/5/2021

Customer Name: Joe Bayne

| CSS/INVOICE# CSS#27682 | DATE(S) OF SERVICE | LOCATION Fort Wadsworth Bldg 358 |
| --- | --- | --- |

| JOB DESCRIPTION removing violations from boiler inspection in order to pass state inspection. Completely re-pipe both safety relief valves on both hydronic type Lockinvar boiler. Both safety relief valves are mounted on a horizontal location. Must repipe safety pressure relief valves on vertical. Existing location can cause sediment to enter safety relief valve and cause relief valve not to function properly. As far as service disconnect on boiler to be able to properly isolate and shut down boiler, there is an isolation safety switch provided by manufacturer located on boiler. This will properly marked to show location of this existing switch. Isolate existing direct vented boiler. Draining down all glycol after isolation of system in order to remove safety pressure relief valve, completely re-pipe to install one relief valve in vertical location. Pump in new glycol (non toxic) to fill up boiler, remove all air out of boiler before opening up to main system. |  |
| --- | --- |
| PARTS 1 ¾ x 6 inch black schedule 40 nipples 1 ¾ black MAL-90 degree elbows 1 ¾ x 16 inch black schedule 40 pipe 1 ¾ black couplings 1 container of leak lock solvent 1 gallon of non toxic antifreeze | COST TOTAL $468.00 |
| LABOR Diagnostic fee for NY024 Sites (one time charge for diagnostic on all boilers) 5 hours 1 mechanic 1 helper | COST $350.00 $700.00 |
| TAX |  |
| TOTAL | $1,518.00 |