| PROPOSAL |  |
| --- | --- |
| INVOICE | X |
| DIAGNOSTIC |  |

Today's Date: 3/25/2021

Customer Name: Joe Bayne

| CSS/INVOICE# CSS#27685 | DATE(S) OF SERVICE | LOCATION Fort Wadsworth Bldg 208 |
| --- | --- | --- |

| JOB DESCRIPTION removing violations from 2 boiler inspection in order to pass state inspection. 2 Triad Boiler, must have proper safety isolation switch located on boiler to properly provide service isolation when providing service or maintenance on boiler. There are presently 1 emergency switches on wall located in mechanical room, however there is no isolation switch present on boiler to shut down during service or maintenance. |  |
| --- | --- |
| PARTS FOR BOTH BOILERS 2 1 4 inch 4x4 junction box 4 Bx fittings 1 Roll Wire #12 gauge 2 single pole isolation switch (20 AMP) | COST TOTAL $300.00 |
| LABOR 8 hours 1 mechanic 1 helper | COST $1,200.00 |
| TAX |  |
| TOTAL | $1,500.00 |