PROPOSAL
INVOICE	X
DIAGNOSTIC

Today's Date: 4/9/2021

Customer Name: Joe Bayne

CSS/INVOICE# / 29818	DATE(S) OF SERVICE	LOCATION / Fort Wadsworth bldg 208

JOB DESCRIPTION / Triad boiler in bldg 208. found system off on safety. Troubleshooted boiler and found air pressure switch defective. Could not jump out pressure switch due to safety reasons. The switch is ordered.
PARTS / 1 air pressure safety switch / Model # for power flame burner JR30A-10	COST / $193.00
LABOR / expediting materials, travel and 1 mechanic x 4 hours	COST / $400.00
Diagnostic Fee	$350.00
TOTAL	$943.00