        Fahrenheit Incorporated Mechanical Contracting
        85 Farless Avenue
        Telephone (732) 673- 9318
        E-mail: Celcius60@aol.com

CMI—Joe BAYNE—fort wadsworth Ny-024-bldg #356—Staten Island N.Y.

      This proposal will be the next phase for CSS#--91366--WO#--20601
Job Description
This proposal is for prevention of coils freezing and rupturing due to power failures when outside air dampers are open during cold outside tempertures causing stagnation of water in heating coil. There are provisions to install glycol to heating system this will require pumping in 50 gallons of glycol into main heating system located in mechanical room on lower level filling up both Triumph condensing boiler as well as verticle type Triad boiler, time will be spent draining entire heating system for all heating coils, pumping in 50 gallons of glycol into entire heating system, removing all air out of entire system to put system back into safe operation. This work should be performed when heating system is no longer needed either before cooling season or before heating system starts. Materials needed---------50gallons--of non toxic antifreeze---Krytech--------$1,589.78----Labor 3days—1- mechanic ----1-helper ------$3,600------Total cost--$5189.78