Both Boilers are down. I was able to get boiler two to come back on by resetting the condensate pump and draining down the condensate tank. Not sure how long it will be before it trips out again. Boiler 2 will not start up, appears to be electrical. Control box does not have green light illuminated. Pump on condensate tank for boiler #1 needs to be replaced. Keeps seizing up, possibly a bad impeller in pump.

Proposal to supply all labor and material needed to complete the following

• Inspect Issue

• Replace pump number 1 at condensate receiver tank

• Leak check.

• Test operation

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY001 |  |  |  |  |  |  |  |  |
| Both Boilers are down |  |  |  |  |  |  |  |  |
| CSS #22792 - CMI # 6916 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 01.08.2020 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 115.00 | 8 |  |  |  |  |  | $ 920.00 |
| 1.2 Motor, pump, assembly & misc |  |  |  |  | $ - | $ - | $ - | $ 2,272.87 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 3,192.87 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |
| 2.2 Misc Charge |  |  |  |  |  |  |  | $ 40.00 |
| CE Factor .9% |  |  |  |  |  |  |  | ($323.29) |
| Grand Total |  |  |  |  |  |  |  | $ 2,909.58 |