Sump pump in boiler room will not turn on. Believe the motor is burnt up.

Proposal to:

- Service call

- Test pumps and evaluate

- Pump #1 has failed bearing and rotted output pipe

- Pump#2 is seized in pump section.

Remove (2) pedestal style pump assemblies and replace with

Cast iron submersible pumps.

Re-plumb sump pit outlet piping to accept submersible pumps

Connect pumps to existing control panel.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY001 |  |  |  |  |  |  |  |  |
| Sump pump in boiler room |  |  |  |  |  |  |  |  |
| CSS #34211 - CMI #16882 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 04.13.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 120.00 | 12 |  |  |  |  |  | $ 1,440.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 4,894.42 |
| 1.3 Misc |  |  |  |  |  |  |  | $ 1,266.88 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 7,601.30 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor .9% |  |  |  |  |  |  |  | $ (760.13) |
| Grand Total |  |  |  |  |  |  |  | $ 6,841.17 |