Facility back-up generator needs additional servicing above what is covered under the FFR contractor. List is as follows: Need 2 - battery racks to move batteries from under back of generator, [can't do battery maintenance without removing batteries from rack]. Exhaust flex cracked, needs to be repaired or replaced. Muffler to engine angle needs to be straightened out first to keep new flex from breaking. Install 24 vdc 15-amp battery charger Rebuild/replace engine starter, or bad Battery [sometimes solenoid just clicks - no crank]. Additional service will ensure the generator will function properly.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Facility back-up generator |  |  |  |  |  |  |  |  |
| CSS #21967 - CMI # 7919 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 11.13.18 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 60 |  |  |  |  |  | $ 6,000.00 |
| 1.2 Materials |  |  |  |  | $ - | $ - | $ - | $ 4,051.93 |
| 1.3 Misc |  |  |  |  |  |  |  | $810.39 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 10,862.32 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.03% |  |  |  |  |  |  |  | $ 325.86 |
| Grand Total |  |  |  |  |  |  |  | $ 11,188.18 |

| Scope of work involved at Onan/ Cummins Diesel 250KW Generator Provide complete Repairs & Regular Service of Onan/ Cummins Generator |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| 1. Remove faulty Engine Starter from unit. Install New Starter, wire to controls |  |  |  |  |  |  |  |
| 2. Install New V-Belts on Unit |  |  |  |  |  |  |  |
| 3. Install New Fuel line filter assembly |  |  |  |  |  |  |  |
| 4. Install New Air Cleaner Element |  |  |  |  |  |  |  |
| 5. Remove Engine Oil from Unit. Install New Engine Oil |  |  |  |  |  |  |  |
| 6. Install New Oil Filter on Engine |  |  |  |  |  |  |  |
| 7. Remove Faulty Batteries and Battery Rack. Relocate to New area of room with |  |  |  |  |  |  |  |
| full access. |  |  |  |  |  |  |  |
| 8. Install New Battery Racks for Generator |  |  |  |  |  |  |  |
| 9. Install New Batteries for Generator |  |  |  |  |  |  |  |
| 10. Install New Wiring to Generator from New battery racks |  |  |  |  |  |  |  |
| 11. Remove Engine coolant from unit |  |  |  |  |  |  |  |
| 12. Replace Engine coolant with Cummins coolant Note: This proposal is a combination of a repair, and a full service Additionally, Moving the battery racks from the unit to a new position will require some work. Also as discussed, per Peter, the exhaust flex hose will not be addressed at this time. |  |  |  |  |  |  |  |