Replace burnt out streetlights.

| Scope of work involved at Bullville USARC CSS33359 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1. Evaluate a Qty of ( 15 ) 30 Foot Pole mounted Security lights on main driveway for repairs |  |  |  |  |  |  |  |  |
| 2. Existing fixtures are Metal Halide HID style. Over 50 % of the existing lights are faulty. |  |  |  |  |  |  |  |  |
| Transformer ballast kits and replacement bulbs would need to be replaced |  |  |  |  |  |  |  |  |
| 3. Existing lighting is 21 years in vintage. Repairs to fixtures does not meet feasibility |  |  |  |  |  |  |  |  |
| due to the cost for replacement parts, and labor to rebuild, and ongoing maintenance of fixtures |  |  |  |  |  |  |  |  |
| Recommended actions would to replace the fixtures with New economical style |  |  |  |  |  |  |  |  |
| energy efficient LED fixtures producing the equivalent lumen levels |  |  |  |  |  |  |  |  |
| 4. Automatic control of lighting needs to be repaired. Lights are currently operating |  |  |  |  |  |  |  |  |
| intermittently during the daytime hours. Photo control for automatic operation is faulty. |  |  |  |  |  |  |  |  |
| PROPOSAL FOR REPLACEMENT/ REPAIRS |  |  |  |  |  |  |  |  |
| 1. Remove faulty lighting fixtures from existing locations. |  |  |  |  |  |  |  |  |
| 2. Install a Qty of ( 15 ) New 150 Watt LED pole mounted lighting fixtures. Provide retrofit |  |  |  |  |  |  |  |  |
| hardware to adapt new lights to existing poles. |  |  |  |  |  |  |  |  |
| 3. Replace photo control & lighting contactor for automatic operation |  |  |  |  |  |  |  |  |

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY011 |  |  |  |  |  |  |  |  |
| Replace burnt out street lights. |  |  |  |  |  |  |  |  |
| CSS #33359 - CMI #16299 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 02.14.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 115.00 | 60 |  |  |  |  |  | $ 6,900.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 8,118.90 |
| 1.3 Equipment Rental - Aerial Boom |  |  |  |  | $ - | $ - | $ - | $ 1,941.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 16,959.90 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  | 1 |  |  |  |  |  | $ 450.00 |
| 2.2 CE Factor .9% |  |  |  |  |  |  |  | ($1,740.99) |
| Grand Total |  |  |  |  |  |  |  | $ 15,668.91 |