Vault behind the AMSA was run incorrectly, voltage in this Vault starts at 277 volts, this included receptacles. ARMAG power has been down completely due to the current situation that the Vault's Power Panel had almost 500 volts running to it.

Removal of existing conduit for the Arms Vault which is wired into a 480-volt switch and the complete installation of a new 1-1/2" conduit run from the sub panel at the arms vault to the 240-volt Circuit breaker panel located in building 124 Electrical Closet. The conduit at the exterior of the building shall be buried in the earth at 24" and consist of rigid conduit. Once in the exterior of the building the conduit shall changeover to 1-1/2'' EMT. A driven grounding electrode conductor shall be driving adjacent to the Arms Vault and bonded to the unit. Branch feeders shall be single phase 240-volt 3 wire consisting of two #2AWG hot legs & one #2AWG neural. The grounding conductor shall be a green #6AWG. Labor rate determined by Davis Beacon Wage

| CMI Cost Estimate |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| NY023 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Vault behind the AMSA was run incorrectly |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CSS #19819 - CMI # 4708 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 9.20.19 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |  |  |  |  |  |  |  |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |  |  |  |  |  |  |  |  |
| 1. Repair Cost |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 1.1 Labor |  |  |  |  |  |  |  | $ 20,500.00 |  |  |  |  |  |  |  |  |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 5,500.00 |  |  |  |  |  |  |  |  |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 26,000.00 |  |  |  |  |  |  |  |  |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ - |  |  |  |  |  |  |  |  |
| 2.2 Truck Charge |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| CE Factor 90% |  |  |  |  |  |  |  | $ (2,600.00) |  |  |  |  |  |  |  |  |
| Grand Total |  |  |  |  |  |  |  | $ 23,400.00 |  |  |  |  |  |  |  |  |