One Triad boiler going off on safety. Triad boiler maintenance, this boiler has no had maintenance performed since the installation date. Completely isolate supply and return lines feeding boiler along with cold water makeup valve. Bring down entire boiler and remove pro type low water cut off and replace with new. Completely disassemble entire gas burner to access combustion chamber, clean combustion chamber, reassemble all components and put back into proper operation.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| One Triad boiler going off on safety. |  |  |  |  |  |  |  |  |
| CSS #27148 - CMI #10373 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 10.14.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 125.00 | 14.6 |  |  |  |  |  | $ 1,825.00 |
| 1.1 Labor Helper | $62.50 | 14.6 |  |  |  |  |  | $ 912.50 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 480.12 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 3,230.12 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor .90% |  |  |  |  |  |  |  | ($323.02) |
| Grand Total |  |  |  |  |  |  |  | $ 2,907.10 |

JOB DESCRIPTION

One Triad boiler going off on safety. Triad boiler maintenance, this boiler has no had maintenance performed since the installation date. Completely isolate supply and return lines feeding boiler along with cold water makeup valve. Bring down entire boiler and remove pro type low water cut off and replace with new. Completely disassemble entire gas burner to access combustion chamber, clean combustion chamber, reassemble all components and put back into proper operation. If any other parts are needed after performing maintenance on this boiler, there will be an extra charge.