Maintenance (overdue) required on the Triad boilers in B208 and B356.  Maintenance includes removing power flame burner and flu piping off top of boiler and other activities.  Not currently covered on PM contract.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Triad boilers in B208 and B356. |  |  |  |  |  |  |  |  |
| CSS #30150 - CMI #12849 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 4.19.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor Boiler Bldg 208 | $ 100.00 | 32.00 |  |  |  |  |  | $ 3,200.00 |
| 1.1 Labor Boiler Bldg 356 | $ 100.00 | 32.00 |  |  |  |  |  | $ 3,200.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 615.00 |
| Total for both boilers |  |  |  |  |  |  |  |  |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 7,015.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.03% |  |  |  |  |  |  |  | $ 210.45 |
| Grand Total |  |  |  |  |  |  |  | $ 7,225.45 |

Boiler in 356 & Bldg 208 need the same maintenance. Bldg 208 & 356 is the same model GPS900-SH, Power Flame JR30 9,00000 BTU natural gas

Presently there are 2 hydronic boilers in bldg 356 & bldg 208, they are a tube type boiler with 1,000000 BTU power flame burner. Must completely remove power flame burner which consists of disconnecting all gas lines, line and low voltage electrical to properly remove burner from boiler. Disconnect breaching on top of boiler, pressure wash all tubes and clean out burner compartment. Reassemble power flame burner, clean electrode, replace high tension wire, reconnect all line and low voltage electric and gas lines to put back into operation.